## Multi-Function Air Source Heat Pump

Air Source Heat Pump » Multi-Function Air Source Heat Pump

Features of Multi-Function Air Source Heat Pump
1. The total COP of multi-function air source heat pump is up to 7.0. 
2. The heat pump can be used both to heat and cool water for winter and summer application and the hot water is produced all year round. 
3. 5 operation modes such as central heating, cooling, cooling plus hot water, central heating plus hot water, or hot water alone are applied for water temperature setting in central heating/cooling and hot water respectively. 
4. In winter, our multi-function air source heat pump heats water and provides floor heating (this is not processed at the same time, in order to avoid deficiency in central heating), with temperature setting for both circuits respectively. Hot water function is available alone after central heating is satisfied.

| Model |  | KFS10- N-LR3 | KFS20- N-LR3 | KFS35- N-LR3 | KFS45- N-LR3 | KFS55- N-LR3 | KFS70- N-LR3 | KFS90- N-LR3 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Power | HP | 3 | 5 | 10 | 12 | 16 | 20 | 25 |
| Hot water capacity | kW | 11.20 | 18.00 | 36.30 | 43.70 | 54.40 | 69.80 | 87.40 |
|  | BTU/h | 38214 | 61416 | 123856 | 149104 | 185613 | 238158 | 298209 |
| Heating capacity | kW | 7.90 | 13.00 | 27.50 | 32.50 | 42.00 | 52.00 | 68.00 |
|  | BTU/h | 26955 | 44356 | 93830 | 110890 | 143304 | 177424 | 232016 |
| Cooling capacity | kW | 7.50 | 12.80 | 25.30 | 31.00 | 40.00 | 50.00 | 65.00 |
|  | BTU/h | 25590 | 43674 | 86324 | 105772 | 136480 | 170600 | 221780 |
| COP |  | 4.67 | 4.62 | 4.65 | 4.62 | 4.69 | 4.58 | 4.64 |
| Rated heated water output | L/h | 241 | 387 | 780 | 939 | 1169 | 1500 | 1879 |
| Rated outlet water temp. | ℃ | 55 |
| Max outlet water temp | ℃ | 60 |
| Heating input power | kW | 2.40 | 3.90 | 7.80 | 9.45 | 11.60 | 15.23 | 18.85 |
| Heating input current | A | 10.91 | 10.26 | 20.53 | 24.87 | 30.53 | 40.08 | 49.61 |
| Cooling input power | kW | 2.60 | 4.02 | 8.26 | 9.70 | 12.50 | 16.00 | 19.00 |
| Cooling input current | A | 11.82 | 10.58 | 21.74 | 25.53 | 32.89 | 42.11 | 50.00 |
| Power supply | V/PH/Hz | 220V~/50Hz | 380V/3N~/50Hz |
| Compressor | Type | Scroll |
|  | Number | 1 | 1 | 2 | 2 | 2 | 2 | 2 |
| Heat exchanger type(water side) |  | Stainless steel brazing plate heat exchanger |
| Heat exchanger type(heat recovery) |  | High efficiency tube in shell heat exchanger |
| Throttling device |  | Emerson thermal expansion valve |
| Fan | Type | Low noise high efficiency axial type |
|  | Discharging | Vertical |
|  | Quantity | 1 | 1 | 2 | 2 | 2 | 2 | 2 |
|  | Power input/W | 70 | 250 | 250 | 250 | 550 | 750 | 750 |
|  | Speed/RPM | 850 | 880 | 880 | 880 | 910 | 940 | 940 |
| Ambient temperature | ℃ | (-10℃~43℃) |
| Refrigerant |  | R22/R407C |
| Noise in 1 meter distance | dB | 59 | 62 | 63 | 63 | 66 | 68 | 68 |
| Water pipe size | inch | R1 | R1 | R1-1/2 | R1-1/2 | Rc2 | Rc2-1/2 | Rc2-1/2 |
| Cabinet |  | Stainless Steel/Steel with powder coated | Steel with powder coated |
| Low pressure protection system |  | Yes |
| High pressure protection system |  | Yes |
| Water flow switch |  | Yes |
| Automatically defrost system |  | Yes |
| Dimension | mm | 710/710 /795 | 810/810 /995 | 1450/705 /1375 | 1450/705 /1375 | 1445/850 /1850 | 1990/980 /2045 | 1990/980 /2045 |
| Package dimension | mm | 810/810 /980 | 920/920 /1080 | 1580/840 /1450 | 1580/840 /1450 | 1580/860 /2000 | 2090/1190 /2145 | 2090/1190 /2145 |
| Net weight | kg | 112 | 137 | 311 | 324 | 406 | 584 | 626 |
| Gross weight | kg | 128 | 160 | 351 | 364 | 466 | 654 | 696 |
| Testing condition |  |  |  |  |  |  |  |  |
| Hot water condition: outdoor temp.(DB/WB) = 20℃/15℃, water temp.(inlet/outlet) = 15℃/55℃. |
| Heating condition: outside temp.(DB/WB) = 7℃/6℃, water temp.(inlet/outlet) = 40℃/45℃. |
| Cooling condition: outside temp.(DB/WB) = 35℃/24℃, water temp.(inlet/outlet) = 7℃/12℃. |

Advantages
1. Our multi-function air source heat pump uses American Copeland scroll compressors. The capacity of the plate heat exchanger and heating, ranges from 11.2~87.4 kW.
2. Our heat pump adopts Technology of National Patent and its energy-saving ranges from 30 to 50% compared to traditional air-conditioner.
3. In summer it produces free sanitary hot water when cooling. In winter sanitary hot water and central heating should be managed synchronously.
4. This product is suitable for ambient temperature of 15~+45℃. 
5. It is reliable with a service life that can reach up to 15 years, featuring low maintenance cost.
6. Our heat pump runs in all weather situations without being affected, no matter in snow or rain weather conditions.
7. Our multi-function air source heat pump is Green with no pollution to the environment.
8. The running cost of the Heat pump supply heat pump can be 75% less than of traditional gas boiler heating system, making it an economic product.
9. It is easy for installation. It can be placed on the roof top, balcony, yard, or basement, thus requiring no special room.
10. This heat pump is anti-corrosion featuring durable coating and it is designed with especial anti-corrosion material.
11. It presents full-automatically start and stop based on water temperature setting.
12. The whole units are warranted for one year period.
13. The heat pump adopts intelligent control system by digital LCD controller.
14. It has 24 hours smooth running, making it operating daily and nightly or in sunny and rainy day situation.

Technical Specification of Multi-Function Air Source Heat Pump

Multi-functional Air Source Heat Pump (heating/cooling+DHW)
Heat pump supply multi-function air source heat pump offers comprehensive eco-energy solution for houses. It is a suitable solution for area that needs floor heating and hot water for application in winter and it can be also applied for cooling water in summer.

As a multi-function air source heat pump manufacturer and supplier in China, Heat pump supply also offers split air source heat pump, domestic heat pump water heater, solar collector, and solar water heater, among others.

http://www.heatpumpsupply.com